## Slide 1
RFI EXECUTIVE SUMMARY REPORT
Civil & MEP Discipline — Impact Analysis, Improvement Recommendations & Structured Tables
Project Reference: P159
Report Date: 20 June 2026
Total RFIs Analysed: 27 | Floors: B1 – 12F
CONFIDENTIAL | Prepared: AI-Assisted Construction PM Analysis

## Slide 2
Overview — RFI Dashboard
Project P159 | 27 RFIs across B1–12F
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
TOTAL RFIs
27
entries analysed
CRITICAL (Open)
2
unresolved / blocked
REJECTED
3+
requiring re-submission
FLOORS AFFECTED
14
B1 through 12F
CIVIL RFIs
10
structural clashes
MEP RFIs
15
drainage / services
ID COORD NEEDED
14
RFIs require ID sign-off
MAX DELAY RISK
8wk
drop panel package
DOMINANT CLASH THEMES
Insufficient shaft sizes
MEP risers (drainage + chilled water) cannot fit in existing shaft openings across 7F–12F
Unauthorised beam penetrations
Pipes proposed through structural beams without sleeves — consultant rejections at 9F/10F
Floor drain / drop panel clashes
Floor traps located above structural drop panels — must be relocated before tiling
Multi-trade coordination gap
14 of 27 RFIs blocked pending ID sub-contractor sign-off — no dedicated coordinator

## Slide 3
Critical RFI #1 — ARC_CRC_KA_042 + ARC_054
7F / 8F (ARC_042) & 9F / 10F (ARC_054) | STATUS: DESIGN DISCUSSION ON-GOING
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
🔴 HIGHEST PRIORITY — FOUR FLOORS BLOCKED — DESIGN INSTRUCTION REQUIRED WITHIN 3 WORKING DAYS
ISSUE DETAIL
What is the problem?
The existing MEP shaft at 7F/8F is undersized. It cannot simultaneously accommodate the DN160 soil/waste drainage riser AND the chilled water pipe riser.
Structural Impact:
Beam L7-B-08 must be physically shifted 500mm downward to clear the BTU meter. This affects:
• Reinforcement schedule: 8LT16@100 + 2LT20@125 bars
• Post-tensioned slab drawings (DM submission)
• Interior design ceiling heights in occupied zones
Proposed Solution:
Enlarge shaft to 1,200 × 450mm clear internal dimension.
Linked RFI:
ARC_054 (9F/10F) carries identical open status — same resolution required.
RISK & REQUIRED ACTION
Schedule Risk
HIGH
Cost Risk
HIGH
Floors Blocked
4 floors (7F, 8F, 9F, 10F)
Delay Estimate
3 – 6 weeks
ACTIONS REQUIRED
1. Escalate to Design Consultant — issue a formal RFI close-out within 3 working days.
2. Obtain written structural engineer instruction confirming beam shift is acceptable.
3. Revise PT drawings to reflect new beam position and shaft dimensions.
4. Update DM submission package before next scheduled authority review.
5. Simultaneously close ARC_054 (9F/10F) with the same instruction.

## Slide 4
Critical RFI #2 — ARC_CRC_KA_056
Floors 9F & 10F | STATUS: ❌ FORMALLY REJECTED — RE-SUBMISSION REQUIRED
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
🔴 CONSULTANT REJECTION — BOTH POINTS NOT ACCEPTED — REVISED PROPOSAL REQUIRED WITHIN 7 DAYS
CONSULTANT REJECTION DETAIL
Contractor Proposal:
Route Ø110mm drainage pipe directly through a structural beam without a sleeve.
Consultant Response — Point 1:
"NOT ACCEPTED. 6" sleeve to be provided for 110 pipe inside beam. Follow the approved structural detail around provided sleeve."
Consultant Response — Point 2:
"NOT ACCEPTED. 6" sleeve to be provided near the proposal for 110 pipe inside beam. Follow the approved structural detail around provided sleeve."
Pattern Risk:
Similar non-compliant proposals exist at ARC_057, ARC_058, and ARC_059 — a systemic issue across multiple floors.
RISK & REQUIRED ACTION
Schedule Risk
MEDIUM-HIGH
Cost Risk
MEDIUM
Re-submission Timeline
7 days
Delay per Floor
2 – 4 weeks
WHAT MUST BE SUBMITTED
1. Revised shop drawings showing 6" sleeve embedded in beam at correct location.
2. Structural reinforcement detail around sleeve (pre-approved standard detail).
3. MEP sub-contractor sign-off confirming pipe routing remains functional.
4. Audited check of ARC_057, ARC_058, ARC_059 for identical violations —
batch re-submission recommended to avoid repeat cycles.

## Slide 5
Critical RFI #3 — ARC_CRC_KA_058
Floors 9F & 10F | STATUS: ⚠️ CONDITIONAL — 4-DOCUMENT PACKAGE REQUIRED
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
⚠️ STRUCTURAL DROP PANEL PENETRATIONS — MULTI-PARTY SUBMISSION BOTTLENECK — 4–8 WEEK DELAY RISK
ISSUE DETAIL
Location:
Structural drop panel at 9F/10F — the most critical load-bearing zone in a PT flat plate.
Pipe Penetrations Required:
• Ø160 Soil Pipe → 8" sleeve
• Ø110 Vent Pipe → 6" sleeve
• Ø160 Waste Pipe → 8" sleeve
Consultant Condition (not yet approved):
A 4-document package must be submitted simultaneously by three separate parties:
1. Tile layout drawing (Tiling Contractor)
2. Distance from vertical elements (Structural Engineer)
3. Structural sleeve reinforcement details (Structural Engineer)
4. Final MEP pipe distribution (MEP Sub-contractor)
Repeat Risk:
Same issue exists at 7F, 8F, 11F, 12F (ARC_041, ARC_066, ARC_069).
RISK & REQUIRED ACTION
Schedule Risk
HIGH
Cost Risk
HIGH
Delay Estimate
4 – 8 weeks
Floors at Risk
7F, 8F, 9F, 10F, 11F, 12F
ACTIONS REQUIRED
1. Convene multi-party coordination meeting within 5 working days:
MEP sub-contractor + Structural Engineer + Tiling Contractor.
2. Appoint a document coordinator to chase all 4 submissions in parallel.
3. Do NOT commence any penetration or sleeve-fixing before written
consultant approval is received — structural failure risk.
4. Apply same process to 7F, 8F, 11F, 12F proactively (batch submission).

## Slide 6
RFI Language Improvement — Before vs. After
Rewriting vague RFI text for faster consultant response
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
RFI REFERENCE
ORIGINAL (UNCLEAR) LANGUAGE
RECOMMENDED (CLEAR) LANGUAGE
ARC_042 7F/8F Shaft + Beam
SHAFT TO BE 1200x450mm TO ACCOMMODATE DRAINAGE AND CHILLED WATER PIPES RISERS
The shaft at Grid [XX-YY], 7F/8F is undersized for the DN160 soil riser and DN[XX] chilled water riser. Contractor proposes 1,200×450mm clear. Please confirm approval and whether beam L7-B-08 shift 500mm downward is structurally acceptable. Response required by [date] to avoid slab pour delay.
ARC_069 11F Beam Penetrations
THE HIGHLIGTED SHAFT WILL REQUIRED VERTICAL AND HORIZONTAL PENETRATIONS FOR THE BEAM, POINT 2 TO BE RESTRICTED AND COORDINATED WITH MEP CONTRACTOR
MEP shaft at Grid [XX], 11F requires beam penetrations for: Ø160 SP (6" sleeve), Ø110 VP (6" sleeve), Ø160 WP (8" sleeve) — see Engineer's Dwg [Ref.]. Please confirm sleeve sizes, edge distances, and reinforcement detailing. MEP contractor requires approval by [date] to maintain programme.
GEN_028 2F–4F Drain Routing
NO OBJECTION TO THE 50MM DRAIN PIPE RUNNING WITH THE FLOOR SCREED TO THE FLOOR TRAP SUBJECT TO PROPER SLOPE AND PROTECTION. HOWEVER THE KITCHEN FLOOR TRAP CURRENTLY LOCATED ABOVE THE DROP PANEL SHALL BE RELOCATED
A Ø50mm drain runs within floor screed at 2F–4F serving the floor trap. Confirm: (a) minimum screed depth and pipe protection spec; (b) required fall/gradient. The kitchen FT at Grid [XX] is above the drop panel — not permitted. Revised FT location shown on Sketch [Ref.], relocated [X]mm from drop panel edge. Please confirm approval.
6 GOLDEN RULES FOR EFFECTIVE RFI WRITING
1. State dimensions and pipe sizes numerically — never 'as highlighted'
2. Separate Background from Question — use distinct headed sections
3. Always include a 'Response Required By' date referencing a programme activity
4. Use sentence case — avoid ALL CAPS text in formal documents
5. Reference related RFIs explicitly by number, not 'as per previous'
6. Every RFI must reference a sketch or drawing — include drawing number

## Slide 7
Table 1 — Civil-Specific RFIs
Schedule & Cost Impact Summary | Project P159
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
RFI NUMBER
LOCATION
ISSUE SUMMARY
STATUS
SCHED. RISK
COST RISK
ACTION
ARC_042 + ARC_054
7F/8F 9F/10F
Beam L7-B-08 shift 500mm + shaft enlarged to 1,200×450mm for drainage & CHW risers
⚠️ Design Discussion On-going
HIGH
HIGH
Escalate to design team within 3 days. Formal instruction required.
ARC_CRC_KA_056
9F, 10F
Ø110 pipe through beam rejected. 6" sleeve + structural detail required
❌ Not Accepted
MEDIUM-HIGH
MEDIUM
Re-submit with correct sleeve detail within 7 days
ARC_CRC_KA_057
7F, 8F
Points 2 & 4 rejected: beam penetration not accepted; shaft extension to 500mm clear
❌ Partially Rejected
MEDIUM
MEDIUM
Revise points 2 & 4 per consultant comments and resubmit
ARC_CRC_KA_058
9F, 10F
Ø160/Ø110 pipes through structural drop panel; 4-document package required
⚠️ Conditional
HIGH
HIGH
Multi-party meeting within 5 days. Do not penetrate before approval.
ARC_CRC_KA_059
10F
6" slab sleeves require 4T16 reinforcement cage (T&B + diagonals) before DM sub.
✅ Cond. Approved
MEDIUM
LOW-MEDIUM
Reflect in PT drawings before DM submission
ARC_CRC_KA_069
11F
Shaft requires vertical & horizontal beam penetrations; MEP impact assessment needed
⚠️ Pending MEP Assess.
MEDIUM-HIGH
MEDIUM
MEP contractor to submit full impact study within 7 days
GEN_CRC_KA_028
2F–4F
Kitchen floor trap above drop panel — must relocate; 50mm drain in screed approved
✅ Cond. Approved
LOW-MEDIUM
LOW
Confirm revised FT location. Coordinate with tiling contractor
ARC_CRC_KA_036
1F
Contractor proposal accepted; cavity must be damp-proofed
✅ Cond. Approved
LOW
LOW
Specify damp-proof system and include in IFC drawings
ARC_CRC_KA_041
7F, 8F
7 shaft modifications: widths extended 250–500mm; sleeves at multiple locations
✅ No Objection
MEDIUM
MEDIUM
Coordinate with formwork; confirm all shaft dims before pour
ARC_CRC_KA_033
1F
Civil interface — insufficient data in log; status unclear
⚠️ No Response
LOW
LOW
Clarify status; re-submit if still pending

## Slide 8
Table 2 — MEP-Specific RFIs (Part 1 of 2)
Schedule & Cost Impact Summary | Project P159
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
RFI NUMBER
LOCATION
DISCIPLINE
ISSUE SUMMARY
STATUS
SCHED.
COST
ACTION
ARC_CRC_KA_042 (MEP aspect)
7F, 8F
Plumbing / Mechanical
Shaft must fit DN160 drainage riser + chilled water riser simultaneously. Linked to beam shift.
⚠️ On-going
HIGH
HIGH
Resolve simultaneously with Civil ARC_042 instruction
ARC_CRC_KA_040
7F, 8F
Plumbing (Floor Traps)
Floor traps moved from beam. ID layout affected. WC FT position needs ID sub-contractor confirmation.
✅ No Objection
LOW-MEDIUM
LOW
Formally notify ID sub-contractor; obtain written confirmation
ARC_CRC_KA_053
B1, B2
MEP (All Services)
Clearance heights +2.70m / +2.50m confirmed in basements only. Separate RFI still needed for Mezzanine/GF.
✅ Approved (Basements)
MEDIUM
LOW
Submit Mezzanine/GF clearance RFI immediately
ARC_CRC_KA_054
9F, 10F
Plumbing / Mechanical
Same shaft/beam clash as ARC_042. Open design discussion — four floors blocked.
⚠️ On-going
HIGH
HIGH
Resolve with ARC_042 — same instruction covers both
ARC_CRC_KA_055
9F, 10F
Plumbing (Shafts)
Follow ARC_040 solution. Tiling coordination required at shaft perimeter on both floors.
✅ Cond. Approved
LOW
LOW
Coordinate with tiling contractor; mark shaft edges on tile drawings
ARC_CRC_KA_063
Multiple
Plumbing (Floor Drains)
Floor drain new locations clash with tile joint layout. Shifts required; tile layout approval is a prerequisite.
✅ Cond. Approved
MEDIUM
LOW-MEDIUM
Obtain approved tile layout before finalising floor drain positions
ARC_CRC_KA_064
11F, 12F
Plumbing (Shaft)
Shaft undersized — extend to minimum 200×200mm clear internal.
✅ Approved
LOW
LOW
Revise formwork drawings; confirm with MEP contractor
ARC_CRC_KA_068
6F
MEP (All Services)
MEP sub-contractor must verify constructability and functionality before any work proceeds.
⚠️ Pending MEP
MEDIUM
MEDIUM
Formally instruct MEP sub-contractor to submit verification within 7 days

## Slide 9
Table 2 — MEP-Specific RFIs (Part 2 of 2)
Schedule & Cost Impact Summary | Project P159
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
RFI NUMBER
LOCATION
DISCIPLINE
ISSUE SUMMARY
STATUS
SCHED.
COST
ACTION
ARC_CRC_KA_065
11F, 12F
Plumbing
Follow GEN_CRC_KA_026 solution and comments — cross-reference approval.
✅ Approved (by ref.)
LOW
LOW
Apply GEN_026 solution; confirm applicability with MEP sub-contractor
ARC_CRC_KA_066
11F
Plumbing (FT)
6" sleeve required for floor trap provision before slab pour.
✅ Approved
LOW
LOW
Procure and install sleeve before slab pour
ARC_CRC_KA_044
7F–10F
Plumbing (Powder Rm)
Powder room drainage approved subject to coordination with ID specialist. Include in IFC drawings.
✅ No Objection
LOW-MEDIUM
LOW
Issue coordination instruction to ID; incorporate in IFC
GEN_CRC_KA_023
1F–6F
Plumbing (Floor Drains)
Floor drain repositioning across 5 floors. Multi-trade coordination with ID and flooring required.
✅ No Objection
MEDIUM
LOW-MEDIUM
Convene multi-trade meeting; lock drain positions before tiling
GEN_CRC_KA_024
2F–6F, 11F–12F
Plumbing (Floor Drains)
8-point floor drain relocation programme across 7 floors — subject to final approval.
✅ Cond. Approved
HIGH
MEDIUM
Submit coordinated drain layout drawing; assign dedicated coordinator
GEN_CRC_KA_026
3F, 4F, 5F
MEP General
Updated layout with extra space submitted. Contractor must confirm clash is cleared.
✅ Cond. Approved
LOW-MEDIUM
LOW
Contractor to formally close out clash clearance check
GEN_CRC_KA_027
2F–6F, 11F–12F
MEP General / Façade
Contractor proposals approved subject to ID and façade coordination across 4 points.
✅ No Objection
MEDIUM
MEDIUM
Initiate tri-party meeting: MEP + ID + Façade contractor
GEN_CRC_KA_029
Multiple
MEP General
General coordination required with ID and all other disciplines. 2 open points.
✅ No Objection
LOW
LOW
Issue coordination instruction; track on weekly RFI register

## Slide 10
Priority Action Register
7 Actions — Ranked P1 to P4 with Target Dates | Project P159
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
PRIORITY
ACTION
RFIs
OWNER
TARGET
STATUS
P1 — URGENT
Escalate ARC_042 & ARC_054 — formal design instruction from consultant required to unblock beam relocation decision
ARC_042 ARC_054
Project Manager + Design Manager
3 working days
🔴 Immediate Escalation Required
P1 — URGENT
Convene multi-party coordination meeting (MEP sub-contractor, Structural Engineer, Tiling Contractor) for drop panel sleeve package
ARC_058
Construction Manager
5 working days
🔴 Meeting Not Yet Scheduled
P2 — HIGH
Re-submit revised beam penetration proposals with correct 6" sleeve and approved structural reinforcement detail
ARC_056 ARC_057
MEP Sub-contractor + Struct. Engineer
7 working days
⚠️ Re-submission Pending
P2 — HIGH
MEP sub-contractor to submit constructability and functionality verification report (6F)
ARC_068
MEP Sub-contractor
7 working days
⚠️ Report Not Submitted
P3 — MEDIUM
Submit separate Mezzanine/GF MEP clearance height RFI (split from ARC_053 — basements only currently approved)
ARC_053
MEP Sub-contractor
10 working days
⚠️ RFI Not Yet Submitted
P3 — MEDIUM
Finalise coordinated floor drain location drawings for 2F–12F; submit for consultant approval
GEN_024 GEN_023
MEP + Tiling Coordinator
14 working days
⚠️ Drawings Pending
P4 — ROUTINE
Issue formal ID coordination instructions for all 'NEED TO COORDINATE WITH ID' RFIs — track on weekly register
ARC_040 ARC_044 ARC_055 GEN_027
Architect / ID Manager
Rolling — weekly
🟡 Ongoing Coordination

## Slide 11
Key Observations & Strategic Recommendations
Root Causes and Systemic Improvements | Project P159
PROJECT P159 | RFI EXECUTIVE SUMMARY | 20 JUNE 2026
CONFIDENTIAL
1
Systemic MEP–Civil Interface Failure
The volume of beam penetration rejections (ARC_056, ARC_057, ARC_058) indicates that MEP shop drawings were not sufficiently coordinated with structural drawings before construction commenced. Recommendation: Conduct a formal BIM/Navisworks clash-detection workshop before proceeding to floors 13F and above to prevent the same pattern repeating.
2
Open Design Discussions During Construction
RFIs ARC_042 and ARC_054 remain open with no resolution timeline — this is a primary cause of programme overruns in construction. Open design decisions must be formally closed with a consultant instruction within 72 hours of escalation. A weekly 'open design items' register should be maintained by the Design Manager.
3
Chain-Reference Risk
Several RFIs close by referencing earlier RFIs (ARC_055 → ARC_040; ARC_065 → GEN_026) without standalone resolution. An error in the base RFI propagates to all referencing floors. All cross-referenced solutions must be formally verified as applicable before acceptance, not assumed equivalent.
4
ID Coordination as a Blocking Factor
"NEED TO COORDINATE WITH ID" appears in 14 of 27 RFIs (52%). Interior design approval is a prerequisite for MEP finalisation on every floor. A dedicated MEP–ID Weekly Coordination Register must be established immediately, with a named coordinator accountable for tracking each item to closure.
5
DM Submission at Risk
RFI ARC_059 explicitly requires that sleeve locations and reinforcement be reflected in PT (Post-Tensioned) drawings PRIOR to DM submission. Any delay resolving structural sleeve positions will hold the DM approval cycle for the entire floor plate — a regulatory risk with potential project-wide programme implications.

## Slide 12
SUMMARY
Three RFIs Demand Immediate Escalation
ARC_042 + ARC_054
Beam shift + shaft enlargement — 4 floors blocked — design instruction required within 3 days
ARC_056
Beam penetration formally rejected — re-submit with correct sleeve detail within 7 days
ARC_058
Drop panel sleeves — 4-party document package — convene coordination meeting within 5 days
Project P159 | RFI Executive Summary | 20 June 2026 | CONFIDENTIAL